## Mappa (hidden)
Piastre Radel Orizzontali
Torna alla ricerca
| Mod. | Profil | Linear | Altezze | [5 empty] | Lunghezze
|  |  |  | 300 | 400 | 500 | 600 | 700 | 900 | 400 | 500 | 600 | 700 | 800 | 900 | 1000 | 1100 | 1200 | 1300 | 1400 | 1500 | 1600 | 1800 | 2000 | 2200 | 2300 | 2400 | 2600 | 2800 | 3000
Igiene | 10 | Buderus | Buderus | 300 | 400 | 500 | 600 | 700 | 900 | 400 | 500 | 600 | 700 | 800 | 900 | 1000 | 1100 | 1200 | - | 1400 | - | 1600 | 1800 | 2000 | - | 2300 | - | 2600 | - | 3000
| 11 | 2017 | N/A | 300 | 400 | 500 | 600 | 700 | 900 | 400 | 500 | 600 | 700 | 800 | 900 | 1000 | 1100 | 1200 | 1300 | 1400 | - | 1600 | 1800 | 2000 | - | 2300 | - | 2600 | - | 3000
Igiene | 20 | Buderus | Buderus | 300 | 400 | 500 | 600 | 700 | 900 | 400 | 500 | 600 | 700 | 800 | 900 | 1000 | 1100 | 1200 | - | 1400 | - | 1600 | 1800 | 2000 | - | 2300 | - | 2600 | - | 3000
| 21 | 2017 | 2017 | 300 | 400 | 500 | 600 | 700 | 900 | 400 | 500 | 600 | 700 | 800 | 900 | 1000 | 1100 | 1200 | - | 1400 | - | 1600 | 1800 | 2000 | - | 2300 | - | 2600 | - | 3000
| 22 | 2013 | 2013 | 300 | 400 | 500 | 600 | 700 | 900 | 400 | 500 | 600 | 700 | 800 | 900 | 1000 | 1100 | 1200 | 1300 | 1400 | - | 1600 | 1800 | 2000 | - | 2300 | - | 2600 | - | 3000
Igiene | 30 | Buderus | Buderus | 300 | 400 | 500 | 600 | 700 | 900 | 400 | 500 | 600 | 700 | 800 | 900 | 1000 | 1100 | 1200 | - | 1400 | - | 1600 | 1800 | 2000 | - | 2300 | - | 2600 | - | 3000
| 33 | 2013 | 2013 | 300 | 400 | 500 | 600 | 700 | 900 | 400 | 500 | 600 | 700 | 800 | 900 | 1000 | 1100 | 1200 | - | 1400 | - | 1600 | 1800 | 2000 | - | 2300 | - | 2600 | - | 3000
| Buderus | = dati analoghi e/o mutuati dai rapporti di prova Buderus
| N/A | = non applicabile / non si fa il modello
| - | = lunghezza non disponibile
Note on T7: pavaninm: esiste la lunghezza 1300 per i modelli 11 e 22, per le altezza 500mm e 600mm - solo per modello compact
Note on T10: pavaninm: esiste la lunghezza 1300 per i modelli 11 e 22, per le altezza 500mm e 600mm - solo per modello compact

## DB (hidden)
[5 empty] | altezza | lunghezza | criteri esistenza
Linear | 10 | 10VL | Vertical Steel Panel radiators - Linear version - Type 10 | Vertical Steel Panel radiators - Linear version - Type 10 | 300 | 300 | H, altezza 300-900, larghezza 400-3000
Profiled | 11 | 11VL | NOT AVAILABLE | Vertical Steel Panel radiators - Linear version - Type 20 | 400 | 400 | V, altezza 1400-2400, larghezza 300-900
| 20 | 20VL | Vertical Steel Panel radiators - Linear version - Type 20 | Vertical Steel Panel radiators - Linear version - Type 21 | 500 | 500 | NOT AVAILABLE
| 21 | 21VL | Vertical Steel Panel radiators - Linear version - Type 21 | Vertical Steel Panel radiators - Linear version - Type 22 | 600 | 600
| 22 | 22VL | Vertical Steel Panel radiators - Linear version - Type 22 | Vertical Steel Panel radiators - profiled version - Type 10 | 700 | 700
| 30 | 30VL | NOT AVAILABLE | Vertical Steel Panel radiators - profiled version - Type 20 | 900 | 800
| 33 | 33VL | NOT AVAILABLE | Vertical Steel Panel radiators - profiled version - Type 21 | 1400 | 900
|  | 10VP | Vertical Steel Panel radiators - profiled version - Type 10 | Vertical Steel Panel radiators - profiled version - Type 22 | 1600 | 1000
|  | 11VP | NOT AVAILABLE | Steel Panel radiator - Linear version - Type 10 | 1800 | 1100
|  | 20VP | Vertical Steel Panel radiators - profiled version - Type 20 | Steel Panel radiator - Linear version - Type 20 | 2000 | 1200
|  | 21VP | Vertical Steel Panel radiators - profiled version - Type 21 | Steel Panel radiator - Linear version - Type 21 | 2200 | 1400
|  | 22VP | Vertical Steel Panel radiators - profiled version - Type 22 | Steel Panel radiator - Linear version - Type 22 | 2400 | 1600
|  | 30VP | NOT AVAILABLE | Steel Panel radiator - Linear version - Type 30 |  | 1800
|  | 33VP | NOT AVAILABLE | Steel Panel radiator - Linear version - Type 33 |  | 2000
|  | 10HL | Steel Panel radiator - Linear version - Type 10 | Steel Panel radiator - profiled version - Type 10 |  | 2300
|  | 11HL | NOT AVAILABLE | Steel Panel radiator - profiled version - Type 11 |  | 2600
|  | 20HL | Steel Panel radiator - Linear version - Type 20 | Steel Panel radiator - profiled version - Type 20 |  | 3000
|  | 21HL | Steel Panel radiator - Linear version - Type 21 | Steel Panel radiator - profiled version - Type 21
|  | 22HL | Steel Panel radiator - Linear version - Type 22 | Steel Panel radiator - profiled version - Type 22
|  | 30HL | Steel Panel radiator - Linear version - Type 30 | Steel Panel radiator - profiled version - Type 30
|  | 32HL | NOT AVAILABLE | Steel Panel radiator - profiled version - Type 33
|  | 33HL | Steel Panel radiator - Linear version - Type 33
|  | 10HP | Steel Panel radiator - profiled version - Type 10
|  | 11HP | Steel Panel radiator - profiled version - Type 11
|  | 20HP | Steel Panel radiator - profiled version - Type 20
|  | 21HP | Steel Panel radiator - profiled version - Type 21
|  | 22HP | Steel Panel radiator - profiled version - Type 22
|  | 30HP | Steel Panel radiator - profiled version - Type 30
|  | 32HP | NOT AVAILABLE
|  | 33HP | Steel Panel radiator - profiled version - Type 33

## Ricerca (hidden)
Hunt Heating Radiator Output Calculator
Thermal output of DLR Steel Panel radiator - profiled version - Type 22 h 600 x L 600 at 60/40/20
| Model |  | Linear/Profiled |  | Height |  | Length
22HP | 22 | H | Profiled |  | 600 | mm | 600 | mm | Steel Panel radiator - profiled version - Type 22 h 600 x L 600
Inlet temperature (110-20°C) |  |  | 60 | °C |  | n | 1.312 |  | Test report | ENE/MRT.RES.13003
Outlet temperature (100-10°C) |  |  | 40 | °C |  | Km | 6.0898 |  | Characteristic curve | Φ = Km x 30^n
Room temperature (5-25°C) |  |  | 20 | °C |  | ΔT | 30 | °C | Thermal output at 60/40/20 | 527.9579 | W
◄ Type 22
◄ Type 10
|  | ◄ Vertical steel panel radiator | [7 empty] | ◄ Type 11
[5 empty] | ▼Horizontal steel panel radiator |  |  |  |  | ◄ Type 20
[5 empty] | ▼Horizontal steel panel radiator |  |  |  |  | ◄ Type 21
◄ Type 22
◄ Type 30
◄ Type 33

## Radel Horizontal
Horizontal Radiator Output Calculator
| Thermal output of DLR Horizontal at following conditions (80/60/20) | [8 empty] | Aggiornamento MP20170223
|  | 10HP | Steel Panel radiator - Profiled Version - Type 10
|  | 11HP | Steel Panel radiator - Profiled Version - Type 11
|  | 20HP | Steel Panel radiator - Profiled Version - Type 20
|  | 21HP | Steel Panel radiator - Profiled Version - Type 21
|  | 22HP | Steel Panel radiator - Profiled Version - Type 22
|  | 30HP | Steel Panel radiator - Profiled Version - Type 30
|  | 33HP | Steel Panel radiator - Profiled Version - Type 33
Select Panel Type |  | 22HP
Enter Inlet temperature (110-20°C) |  | 80 | °C
Enter Outlet temperature (100-10°C) |  | 60 | °C |  |  | Delta.Temp (ΔT) | 50
Enter Room temperature (5-25°C) |  | 20 | °C |  |  | Characteristic Curve | Φ = Km x50^n
| Height [mm] | 300 | 400 | 500 | 600 | 700 | 900
| Length [mm] | [6 empty] | Test report
|  | 22HP300 | 22HP400 | 22HP500 | 22HP600 | 22HP700 | 22HP900
| 300 | 299.2711 | 373.526 | 445.3892 | 515.985 | 585.9641 | 725.8619 | ENE/MRT.RES.13003 | Type 22 ►
| 400 | 399.0282 | 498.0346 | 593.8523 | 687.98 | 781.2855 | 967.8159
| 500 | 498.7852 | 622.5433 | 742.3153 | 859.975 | 976.6069 | 1209.7699
| 600 | 598.5423 | 747.0519 | 890.7784 | 1031.9701 | 1171.9283 | 1451.7239
| 700 | 698.2993 | 871.5606 | 1039.2415 | 1203.9651 | 1367.2496 | 1693.6779 | Type 10 ►
| 800 | 798.0564 | 996.0693 | 1187.7046 | 1375.9601 | 1562.571 | 1935.6318
| 900 | 897.8134 | 1120.5779 | 1336.1676 | 1547.9551 | 1757.8924 | 2177.5858 | Type 11 ►
| 1000 | 997.5705 | 1245.0866 | 1484.6307 | 1719.9501 | 1953.2138 | 2419.5398
| 1100 | 1097.3275 | 1369.5952 | 1633.0938 | 1891.9451 | 2148.5351 | 2661.4938 | Type 20 ►
| 1200 | 1197.0846 | 1494.1039 | 1781.5568 | 2063.9401 | 2343.8565 | 2903.4478
| 1400 | 1396.5987 | 1743.1212 | 2078.483 | 2407.9301 | 2734.4993 | 3387.3557 | Type 21 ►
| 1600 | 1596.1128 | 1992.1385 | 2375.4091 | 2751.9202 | 3125.142 | 3871.2637
| 1800 | 1795.6269 | 2241.1558 | 2672.3352 | 3095.9102 | 3515.7848 | 4355.1716 | Type 22 ►
| 2000 | 1995.141 | 2490.1731 | 2969.2614 | 3439.9002 | 3906.4275 | 4839.0796
| 2300 | 2294.4121 | 2863.6991 | 3414.6506 | 3955.8852 | 4492.3917 | 5564.9415 | Type 30 ►
| 2600 | 2593.6832 | 3237.2251 | 3860.0398 | 4471.8702 | 5078.3558 | 6290.8035
| 3000 | 2992.7114 | 3735.2597 | 4453.8921 | 5159.8503 | 5859.6413 | 7258.6194 | Type 33 ►
| Km | 6.2511 | 7.6474 | 8.9382 | 10.1496 | 11.1973 | 13.0898
| n | 1.2967 | 1.3018 | 1.3069 | 1.312 | 1.3194 | 1.3342

## --TUTTI-- (hidden)
ID | 10HP300 | 10HP400 | 10HP500 | 10HP600 | 10HP700 | 10HP900 | 11HP300 | 11HP400 | 11HP500 | 11HP600 | 11HP700 | 11HP900 | 20HP300 | 20HP400 | 20HP500 | 20HP600 | 20HP700 | 20HP900 | 21HP300 | 21HP400 | 21HP500 | 21HP600 | 21HP700 | 21HP900 | 22HP300 | 22HP400 | 22HP500 | 22HP600 | 22HP700 | 22HP900 | 30HP300 | 30HP400 | 30HP500 | 30HP600 | 30HP700 | 30HP900 | 32HP300 | 32HP400 | 32HP500 | 32HP600 | 32HP700 | 32HP900 | 33HP300 | 33HP400 | 33HP500 | 33HP600 | 33HP700 | 33HP900 | 10HL300 | 10HL400 | 10HL500 | 10HL600 | 10HL700 | 10HL900 | 20HL300 | 20HL400 | 20HL500 | 20HL600 | 20HL700 | 20HL900 | 21HL300 | 21HL400 | 21HL500 | 21HL600 | 21HL700 | 21HL900 | 22HL300 | 22HL400 | 22HL500 | 22HL600 | 22HL700 | 22HL900 | 30HL300 | 30HL400 | 30HL500 | 30HL600 | 30HL700 | 30HL900 | 33HL300 | 33HL400 | 33HL500 | 33HL600 | 33HL700 | 33HL900
Piastre Radel Orizzontali Profilate e Linear | 10HP | 10HP | 10HP | 10HP | 10HP | 10HP | 11HP | 11HP | 11HP | 11HP | 11HP | 11HP | 20HP | 20HP | 20HP | 20HP | 20HP | 20HP | 21HP | 21HP | 21HP | 21HP | 21HP | 21HP | 22HP | 22HP | 22HP | 22HP | 22HP | 22HP | 30HP | 30HP | 30HP | 30HP | 30HP | 30HP | 32HP | 32HP | 32HP | 32HP | 32HP | 32HP | 33HP | 33HP | 33HP | 33HP | 33HP | 33HP | 10HL | 10HL | 10HL | 10HL | 10HL | 10HL | 20HL | 20HL | 20HL | 20HL | 20HL | 20HL | 21HL | 21HL | 21HL | 21HL | 21HL | 21HL | 22HL | 22HL | 22HL | 22HL | 22HL | 22HL | 30HL | 30HL | 30HL | 30HL | 30HL | 30HL | 33HL | 33HL | 33HL | 33HL | 33HL | 33HL
Mod. | Igiene 10 | Igiene 11 | Igiene 12 | Igiene 13 | Igiene 14 | Igiene 15 | Compact 11 | Compact 12 | Compact 13 | Compact 14 | Compact 15 | Compact 16 | Igiene 20 | Igiene 21 | Igiene 22 | Igiene 23 | Igiene 24 | Igiene 25 | Compact 21 | Compact 22 | Compact 23 | Compact 24 | Compact 25 | Compact 26 | Compact 22 | Compact 23 | Compact 24 | Compact 25 | Compact 26 | Compact 27 | Igiene 30 | Igiene 31 | Igiene 32 | Igiene 33 | Igiene 34 | Igiene 35 | Compact 32 | Compact 33 | Compact 34 | Compact 35 | Compact 36 | Compact 37 | Compact 33 | Compact 34 | Compact 35 | Compact 36 | Compact 37 | Compact 38 | Linear 10 | Linear 11 | Linear 12 | Linear 13 | Linear 14 | Linear 15 | Linear 20 | Linear 21 | Linear 22 | Linear 23 | Linear 24 | Linear 25 | Linear 21 | Linear 22 | Linear 23 | Linear 24 | Linear 25 | Linear 26 | Linear 22 | Linear 23 | Linear 24 | Linear 25 | Linear 26 | Linear 27 | Linear 30 | Linear 31 | Linear 32 | Linear 33 | Linear 34 | Linear 35 | Linear 33 | Linear 34 | Linear 35 | Linear 36 | Linear 37 | Linear 38
TR | ENE/MRT.RES.13013 | ENE/MRT.RES.13013 | ENE/MRT.RES.13013 | ENE/MRT.RES.13013 | ENE/MRT.RES.13013 | ENE/MRT.RES.13013 | ENE/MRT.RES.17005 | ENE/MRT.RES.17005 | ENE/MRT.RES.17005 | ENE/MRT.RES.17005 | ENE/MRT.RES.17005 | ENE/MRT.RES.17005 | ENE/MRT.RES.13016_a | ENE/MRT.RES.13016_a | ENE/MRT.RES.13016_a | ENE/MRT.RES.13016_a | ENE/MRT.RES.13016_a | ENE/MRT.RES.13016_a | ENE/MRT.RES.17006 | ENE/MRT.RES.17006 | ENE/MRT.RES.17006 | ENE/MRT.RES.17006 | ENE/MRT.RES.17006 | ENE/MRT.RES.17006 | ENE/MRT.RES.13003 | ENE/MRT.RES.13003 | ENE/MRT.RES.13003 | ENE/MRT.RES.13003 | ENE/MRT.RES.13003 | ENE/MRT.RES.13003 | ENE/MRT.RES.13017_a | ENE/MRT.RES.13017_a | ENE/MRT.RES.13017_a | ENE/MRT.RES.13017_a | ENE/MRT.RES.13017_a | ENE/MRT.RES.13017_a | manca TR | manca TR | manca TR | manca TR | manca TR | manca TR | ENE/MRT.RES.13004 | ENE/MRT.RES.13004 | ENE/MRT.RES.13004 | ENE/MRT.RES.13004 | ENE/MRT.RES.13004 | ENE/MRT.RES.13004 | ENE/MRT.RES.13027_a | ENE/MRT.RES.13027_a | ENE/MRT.RES.13027_a | ENE/MRT.RES.13027_a | ENE/MRT.RES.13027_a | ENE/MRT.RES.13027_a | ENE/MRT.RES.13028_a | ENE/MRT.RES.13028_a | ENE/MRT.RES.13028_a | ENE/MRT.RES.13028_a | ENE/MRT.RES.13028_a | ENE/MRT.RES.13028_a | ENE/MRT.RES.17007 | ENE/MRT.RES.17007 | ENE/MRT.RES.17007 | ENE/MRT.RES.17007 | ENE/MRT.RES.17007 | ENE/MRT.RES.17007 | ENE/MRT.RES.13011 | ENE/MRT.RES.13011 | ENE/MRT.RES.13011 | ENE/MRT.RES.13011 | ENE/MRT.RES.13011 | ENE/MRT.RES.13011 | ENE/MRT.RES.13021_a | ENE/MRT.RES.13021_a | ENE/MRT.RES.13021_a | ENE/MRT.RES.13021_a | ENE/MRT.RES.13021_a | ENE/MRT.RES.13021_a | ENE/MRT.RES.13012 | ENE/MRT.RES.13012 | ENE/MRT.RES.13012 | ENE/MRT.RES.13012 | ENE/MRT.RES.13012 | ENE/MRT.RES.13012
Altezza | 300 | 400 | 500 | 600 | 700 | 900 | 300 | 400 | 500 | 600 | 700 | 900 | 300 | 400 | 500 | 600 | 700 | 900 | 300 | 400 | 500 | 600 | 700 | 900 | 300 | 400 | 500 | 600 | 700 | 900 | 300 | 400 | 500 | 600 | 700 | 900 | 300 | 400 | 500 | 600 | 700 | 900 | 300 | 400 | 500 | 600 | 700 | 900 | 300 | 400 | 500 | 600 | 700 | 900 | 300 | 400 | 500 | 600 | 700 | 900 | 300 | 400 | 500 | 600 | 700 | 900 | 300 | 400 | 500 | 600 | 700 | 900 | 300 | 400 | 500 | 600 | 700 | 900 | 300 | 400 | 500 | 600 | 700 | 900
RESA | 340 | 442.3 | 540.8 | 635.8 | 727.7 | 902.4 | 569.8 | 707.2 | 842.3 | 977.4 | 1113.9 | 1395 | 576.078 | 709.459 | 842.8289 | 978.7795 | 1118.9394 | 1416.6195 | 789.6 | 1001.1 | 1204.6 | 1402.5 | 1596 | 1973.8 | 997.6 | 1245.1 | 1484.7 | 1720 | 1953.2 | 2419.5 | 837.1704 | 1042.674 | 1241.2135 | 1435.9691 | 1628.8305 | 2013.7506 | [6 empty] | 1451.5 | 1799.7 | 2132 | 2453.6 | 2768 | 3383.6 | 291.8 | 355.8 | 425.5 | 502.9 | 589.4 | 795.9 | 515.0597 | 649.1696 | 780.3297 | 910.2997 | 1040.1929 | 1302.5494 | 764.2 | 953.9 | 1139.7 | 1324.5 | 1510.1 | 1888.4 | 956.7 | 1194.1 | 1423 | 1646.7 | 1867.6 | 2305.8 | 780.29 | 975.3497 | 1165.4101 | 1353.3405 | 1540.9509 | 1919.7403 | 1413.3 | 1740.7 | 2058.2 | 2371.6 | 2684.5 | 3318
Km | 1.8008 | 2.5347 | 3.3536 | 4.2667 | 4.7794 | 5.6781 | 4.1542 | 5.0316 | 5.8479 | 6.6216 | 7.4272 | 9.0099 | 3.9075 | 4.7382 | 5.5427 | 6.3378 | 7.2018 | 9.0085 | 5.7099 | 6.955 | 8.0407 | 8.9939 | 9.9091 | 11.4866 | 6.2511 | 7.6474 | 8.9382 | 10.1496 | 11.1973 | 13.0898 | 5.4889 | 6.5463 | 7.4625 | 8.2672 | 9.4073 | 11.7044 | [6 empty] | 10.0113 | 11.7001 | 13.0634 | 14.17 | 15.3583 | 17.329 | 1.9527 | 2.3742 | 2.8321 | 3.3375 | 4.2089 | 6.5815 | 3.0692 | 4.1921 | 5.461 | 6.9038 | 7.7917 | 9.5183 | 5.8723 | 7.0945 | 8.204 | 9.2279 | 10.2492 | 12.164 | 6.1037 | 7.5634 | 8.948 | 10.2803 | 11.1688 | 12.6546 | 5.2284 | 6.5219 | 7.7767 | 9.012 | 10.0543 | 12.026 | 9.1473 | 10.9905 | 12.6772 | 14.2502 | 15.5989 | 18.0299
n | 1.3396 | 1.3195 | 1.2993 | 1.2792 | 1.2846 | 1.2956 | 1.2579 | 1.2642 | 1.2705 | 1.2767 | 1.2808 | 1.2889 | 1.2764 | 1.2804 | 1.2843 | 1.2883 | 1.2898 | 1.2929 | 1.26 | 1.2703 | 1.2805 | 1.2908 | 1.299 | 1.3156 | 1.2967 | 1.3018 | 1.3069 | 1.312 | 1.3194 | 1.3342 | 1.2851 | 1.2962 | 1.3072 | 1.3183 | 1.3175 | 1.3159 | [6 empty] | 1.2721 | 1.2873 | 1.3024 | 1.3175 | 1.3278 | 1.3482 | 1.2798 | 1.2806 | 1.2813 | 1.282 | 1.2632 | 1.2258 | 1.3095 | 1.289 | 1.2684 | 1.2479 | 1.251 | 1.2574 | 1.2445 | 1.2529 | 1.2612 | 1.2696 | 1.2763 | 1.2896 | 1.2921 | 1.2939 | 1.2958 | 1.2976 | 1.3086 | 1.3305 | 1.2795 | 1.2801 | 1.2806 | 1.2811 | 1.2863 | 1.2967 | 1.2884 | 1.2947 | 1.3011 | 1.3074 | 1.316 | 1.3331

## Radel Vertical
Vertical Radiator Output Calculator
Thermal output of DLR at (55/45/20)
|  | 10VP | Vertical Steel Panel radiators - Profiled Version - Type 10
|  | 20VP | Vertical Steel Panel radiators - Profiled Version - Type 20
|  | 21VP | Vertical Steel Panel radiators - Profiled Version - Type 21
|  | 22VP | Vertical Steel Panel radiators - Profiled Version - Type 22
Select Panel Type |  | 21VP
| Enter Inlet temperature (110-20°C) | 55 |  | °C
| Enter Outlet temperature (100-10°C) | 45 |  | °C | [5 empty] | Delta.Temp (ΔT) |  | 30
| Enter Room temperature (5-25°C) | 20 |  | °C | [5 empty] | Characteristic Curve |  | Φ = Km x30^n
Test conditions ΔT30 according to EN 442 are 55/45/20; related thermal outputs on Catalogue
| Height [mm] | 1400 | 1500 | 1600 | 1700 | 1800 | 1900 | 2000 | 2100 | 2200 | 2300 | 2400
| Length [mm] | [11 empty] | Type 10 ►
| ID | 21VP1400 | 21VP1500 | 21VP1600 | 21VP1700 | 21VP1800 | 21VP1900 | 21VP2000 | 21VP2100 | 21VP2200 | 21VP2300 | 21VP2400
| 1 wet chanel (33,33) | 46.0232 | 0 | 49.8948 | 0 | 53.5622 | 0 | 58.028 | 0 | 62.4776 | 64.7018 | 66.888
| 300 | 414.2086 | 0 | 449.0528 | 0 | 482.0601 | 0 | 522.2517 | 0 | 562.298 | 582.3165 | 601.9921 |  | Type 21 ►
| 400 | 552.2781 | 0 | 598.7371 | 0 | 642.7468 | 0 | 696.3356 | 0 | 749.7306 | 776.422 | 802.6562 | Type 20 ►
| 500 | 690.3477 | 0 | 748.4213 | 0 | 803.4335 | 0 | 870.4195 | 0 | 937.1633 | 970.5275 | 1003.3202 | Type 11 ►
| 600 | 828.4172 | 0 | 898.1056 | 0 | 964.1202 | 0 | 1044.5035 | 0 | 1124.596 | 1164.633 | 1203.9842 | Type 21 ►
| 700 | 966.4868 | 0 | 1047.7899 | 0 | 1124.8069 | 0 | 1218.5874 | 0 | 1312.0286 | 1358.7385 | 1404.6483
| 900 | 1242.6258 | 0 | 1347.1584 | 0 | 1446.1803 | 0 | 1566.7552 | 0 | 1686.8939 | 1746.9495 | 1805.9764 | Type 22 ►
| Km | 0.56376 | 0 | 0.5561 | 0 | 0.54319 | 0 | 0.59904 | 0 | 0.65655 | 0.68601 | 0.71255
| n | 1.2943 | 0 | 1.3221 | 0 | 1.3499 | 0 | 1.3446 | 0 | 1.3394 | 1.3368 | 1.3354
| Test report | ENE/MRT.RES.00012d | ENE/MRT.RES.00012d | ENE/MRT.RES.00012d | ENE/MRT.RES.00012d | ENE/MRT.RES.00012d | ENE/MRT.RES.00012d | ENE/MRT.RES.00012d | ENE/MRT.RES.00012d | ENE/MRT.RES.15027 | ENE/MRT.RES.00012d | ENE/MRT.RES.15027

## Linear Horizonal
Linear Horizontal Radiator Output Calculator
| Thermal output of DLR Horizontal at following conditions (80/60/20) | [8 empty] | Aggiornamento MP20170223
|  | 10HL | Steel Panel radiator - Linear Version - Type 10
|  | 20HL | Steel Panel radiator - Linear Version - Type 20
|  | 21HL | Steel Panel radiator - Linear Version - Type 21
|  | 22HL | Steel Panel radiator - Linear Version - Type 22
|  | 30HL | Steel Panel radiator - Linear Version - Type 30
|  | 33HL | Steel Panel radiator - Linear Version - Type 33
Select Panel Type |  | 22HL
Enter Inlet temperature (110-20°C) |  | 80 | °C
Enter Outlet temperature (100-10°C) |  | 60 | °C |  |  | Delta.Temp (ΔT) | 50
Enter Room temperature (5-25°C) |  | 20 | °C |  |  | Characteristic Curve | Φ = Km x50^n
| Height [mm] | 300 | 400 | 500 | 600 | 700 | 900
| Length [mm] | [6 empty] | Test report
|  | 22HL300 | 22HL400 | 22HL500 | 22HL600 | 22HL700 | 22HL900
| 300 | 287.001 | 358.2223 | 426.8936 | 494.019 | 560.2753 | 691.7278 | ENE/MRT.RES.13011 | Type 22 ►
| 400 | 382.6681 | 477.6297 | 569.1915 | 658.692 | 747.0337 | 922.3038
| 500 | 478.3351 | 597.0371 | 711.4893 | 823.365 | 933.7922 | 1152.8797
| 600 | 574.0021 | 716.4446 | 853.7872 | 988.038 | 1120.5506 | 1383.4556
| 700 | 669.6691 | 835.852 | 996.0851 | 1152.711 | 1307.309 | 1614.0316 | Type 10 ►
| 800 | 765.3361 | 955.2594 | 1138.383 | 1317.384 | 1494.0674 | 1844.6075
| 900 | 861.0031 | 1074.6669 | 1280.6808 | 1482.057 | 1680.8259 | 2075.1835 | Type 11 ►
| 1000 | 956.6702 | 1194.0743 | 1422.9787 | 1646.73 | 1867.5843 | 2305.7594
| 1100 | 1052.3372 | 1313.4817 | 1565.2766 | 1811.403 | 2054.3427 | 2536.3354 | Type 20 ►
| 1200 | 1148.0042 | 1432.8891 | 1707.5744 | 1976.076 | 2241.1012 | 2766.9113
| 1400 | 1339.3382 | 1671.704 | 1992.1702 | 2305.422 | 2614.618 | 3228.0632 | Type 21 ►
| 1600 | 1530.6723 | 1910.5189 | 2276.7659 | 2634.768 | 2988.1349 | 3689.2151
| 1800 | 1722.0063 | 2149.3337 | 2561.3616 | 2964.114 | 3361.6518 | 4150.3669 | Type 22 ►
| 2000 | 1913.3403 | 2388.1486 | 2845.9574 | 3293.46 | 3735.1686 | 4611.5188
| 2300 | 2200.3414 | 2746.3709 | 3272.851 | 3787.479 | 4295.4439 | 5303.2467 | Type 30 ►
| 2600 | 2487.3424 | 3104.5932 | 3699.7446 | 4281.498 | 4855.7192 | 5994.9745
| 3000 | 2870.0105 | 3582.2229 | 4268.9361 | 4940.19 | 5602.7529 | 6917.2782 | Type 33 ►
| Km | 6.1037 | 7.5634 | 8.948 | 10.2803 | 11.1688 | 12.6546
| n | 1.2921 | 1.2939 | 1.2958 | 1.2976 | 1.3086 | 1.3305

## Linear Vertical
Vertical Radiator Output Calculator
Thermal output of DLR at (85/75/20)
|  | 10VL | Vertical Steel Panel radiators - Linear Version - Type 10
|  | 20VL | Vertical Steel Panel radiators - Linear Version - Type 20
|  | 21VL | Vertical Steel Panel radiators - Linear Version - Type 21
|  | 22VL | Vertical Steel Panel radiators - Linear Version - Type 22
Select Panel Type |  | 22VL
Enter Inlet temperature (110-20°C) |  | 85 |  | °C
Enter Outlet temperature (100-10°C) |  | 75 |  | °C | [5 empty] | Delta.Temp (ΔT) |  | 60
Enter Room temperature (5-25°C) |  | 20 |  | °C | [5 empty] | Characteristic Curve |  | Φ = Km x60^n
| Height [mm] | 1400 | 1500 | 1600 | 1700 | 1800 | 1900 | 2000 | 2100 | 2200 | 2300 | 2400
| Length [mm] | [11 empty] | Type 10 ►
| ID | 22VL1400 | 22VL1500 | 22VL1600 | 22VL1700 | 22VL1800 | 22VL1900 | 22VL2000 | 22VL2100 | 22VL2200 | 22VL2300 | 22VL2400
| 1 wet chanel (33,33) | 135.5377 | 142.7287 | 149.751 | 156.6217 | 163.3274 | 169.9118 | 176.3597 | 182.6567 | 188.839 | 195.1729 | 201.3883
| 300 | 1219.8391 | 1284.5585 | 1347.7586 | 1409.595 | 1469.9462 | 1529.2065 | 1587.2376 | 1643.91 | 1699.5514 | 1756.5559 | 1812.4949 |  | Type 22 ►
| 400 | 1626.4522 | 1712.7447 | 1797.0115 | 1879.46 | 1959.9282 | 2038.942 | 2116.3168 | 2191.88 | 2266.0686 | 2342.0746 | 2416.6599 | Type 20 ►
| 500 | 2033.0652 | 2140.9309 | 2246.2643 | 2349.325 | 2449.9103 | 2548.6775 | 2645.396 | 2739.8499 | 2832.5857 | 2927.5932 | 3020.8249 | Type 11 ►
| 600 | 2439.6782 | 2569.1171 | 2695.5172 | 2819.19 | 2939.8924 | 3058.413 | 3174.4752 | 3287.8199 | 3399.1029 | 3513.1119 | 3624.9899 | Type 21 ►
| 700 | 2846.2913 | 2997.3033 | 3144.7701 | 3289.055 | 3429.8744 | 3568.1486 | 3703.5544 | 3835.7899 | 3965.62 | 4098.6305 | 4229.1549
| 900 | 3659.5173 | 3853.6756 | 4043.2758 | 4228.785 | 4409.8385 | 4587.6196 | 4761.7129 | 4931.7299 | 5098.6543 | 5269.6678 | 5437.4848 | Type 22 ►
| Km | 0.52925 | 0.5566 | 0.58322 | 0.60918 | 0.63443 | 0.65766 | 0.68019 | 0.702 | 0.72318 | 0.72196 | 0.71956
| n | 1.3544 | 1.3548 | 1.3551 | 1.3554 | 1.3557 | 1.3566 | 1.3575 | 1.3583 | 1.3592 | 1.3677 | 1.3761
| Test report | ENE/MRT.RES.15020 | ENE/MRT.RES.15020 | ENE/MRT.RES.15020 | ENE/MRT.RES.15020 | ENE/MRT.RES.15020 | ENE/MRT.RES.15020 | ENE/MRT.RES.15020 | ENE/MRT.RES.15020 | ENE/MRT.RES.15020 | ENE/MRT.RES.15020 | ENE/MRT.RES.15020

## Safe Touch Horizontal
Safe Touch Horizontal Radiator Output Calculator
Aggiornamento MP20170223
|  | 10HP | Steel Panel radiator - Profiled Version - Type 10
|  | 11HP | Steel Panel radiator - Profiled Version - Type 11
|  | 20HP | Steel Panel radiator - Profiled Version - Type 20
|  | 21HP | Steel Panel radiator - Profiled Version - Type 21
|  | 22HP | Steel Panel radiator - Profiled Version - Type 22
|  | 30HP | Steel Panel radiator - Profiled Version - Type 30
|  | 33HP | Steel Panel radiator - Profiled Version - Type 33
Select Panel Type |  | 22HP
Enter Inlet temperature (110-20°C) |  | 80 | °C
Enter Outlet temperature (100-10°C) |  | 60 | °C |  |  | Delta.Temp (ΔT) | 48
Enter Room temperature (5-25°C) |  | 22 | °C |  |  | Characteristic Curve | Φ = Km x48^n
| Height [mm] | 300 | 400 | 500 | 600 | 700 | 900
| Length [mm] | [6 empty] | Test report
|  | 22HP300 | 22HP400 | 22HP500 | 22HP600 | 22HP700 | 22HP900
| 300 | 278.1652 | 347.1106 | 413.8055 | 479.295 | 544.1337 | 673.6371 | ENE/MRT.RES.13003 | Type 22 ►
| 400 | 370.8869 | 462.8142 | 551.7406 | 639.0599 | 725.5115 | 898.1829
| 500 | 463.6086 | 578.5177 | 689.6758 | 798.8249 | 906.8894 | 1122.7286
| 600 | 556.3303 | 694.2213 | 827.6109 | 958.5899 | 1088.2673 | 1347.2743
| 700 | 649.052 | 809.9248 | 965.5461 | 1118.3549 | 1269.6452 | 1571.82 | Type 10 ►
| 800 | 741.7738 | 925.6284 | 1103.4812 | 1278.1199 | 1451.0231 | 1796.3657
| 900 | 834.4955 | 1041.3319 | 1241.4164 | 1437.8849 | 1632.401 | 2020.9114 | Type 11 ►
| 1000 | 927.2172 | 1157.0355 | 1379.3515 | 1597.6498 | 1813.7789 | 2245.4571
| 1100 | 1019.9389 | 1272.739 | 1517.2867 | 1757.4148 | 1995.1568 | 2470.0029 | Type 20 ►
| 1200 | 1112.6606 | 1388.4425 | 1655.2218 | 1917.1798 | 2176.5346 | 2694.5486
| 1400 | 1298.1041 | 1619.8496 | 1931.0921 | 2236.7098 | 2539.2904 | 3143.64 | Type 21 ►
| 1600 | 1483.5475 | 1851.2567 | 2206.9625 | 2556.2398 | 2902.0462 | 3592.7314
| 1800 | 1668.991 | 2082.6638 | 2482.8328 | 2875.7697 | 3264.802 | 4041.8229 | Type 22 ►
| 2000 | 1854.4344 | 2314.0709 | 2758.7031 | 3195.2997 | 3627.5577 | 4490.9143
| 2300 | 2132.5996 | 2661.1816 | 3172.5085 | 3674.5946 | 4171.6914 | 5164.5514 | Type 30 ►
| 2600 | 2410.7647 | 3008.2922 | 3586.314 | 4153.8896 | 4715.8251 | 5838.1886
| 3000 | 2781.6516 | 3471.1064 | 4138.0546 | 4792.9495 | 5441.3366 | 6736.3714 | Type 33 ►
| Km | 6.1261 | 7.4945 | 8.7595 | 9.9466 | 10.9733 | 12.828
| n | 1.2967 | 1.3018 | 1.3069 | 1.312 | 1.3194 | 1.3342
2%

## Safe Touch Vertical
Safe Touch Vertical Radiator Output Calculator
10VP
20VP
21VP
22VP
Select Panel Type |  | 22VP
Enter Inlet temperature (110-20°C) |  | 85 | °C
Enter Outlet temperature (100-10°C) |  | 75 | °C | [5 empty] | Delta.Temp (ΔT) |  | 60
Enter Room temperature (5-25°C) |  | 20 | °C | [5 empty] | Characteristic Curve |  | Φ = Km x60^n
| Height [mm] | 1400 | 1600 | 1700 | 1800 | 1900 | 2000 | 2100 | 2200 | 2300 | 2400
| Length [mm] | [10 empty] | Type 10 ►
| ID | 22VP1400 | 22VP1600 | 22VP1700 | 22VP1800 | 22VP1900 | 22VP2000 | 22VP2100 | 22VP2200 | 22VP2300 | 22VP2400
| 1 wet chanel (33,33) | 137.4506 | 149.5112 | 159.0509 | 162.4522 | 173.234 | 177.3742 | 189.0627 | 193.52 | 206.2135 | 210.9718
| 300 | 1237.0551 | 1345.6004 | 1431.4583 | 1462.07 | 1559.1056 | 1596.3676 | 1701.5645 | 1741.6802 | 1855.9213 | 1898.7466 |  | Type 22 ►
| 400 | 1649.4068 | 1794.1339 | 1908.6111 | 1949.4267 | 2078.8075 | 2128.4901 | 2268.7527 | 2322.2403 | 2474.5618 | 2531.6621 | Type 20 ►
| 500 | 2061.7586 | 2242.6674 | 2385.7638 | 2436.7834 | 2598.5094 | 2660.6127 | 2835.9408 | 2902.8004 | 3093.2022 | 3164.5776
| 600 | 2474.1103 | 2691.2009 | 2862.9166 | 2924.1401 | 3118.2113 | 3192.7352 | 3403.129 | 3483.3605 | 3711.8427 | 3797.4931 | Type 21 ►
| 700 | 2886.462 | 3139.7344 | 3340.0694 | 3411.4967 | 3637.9131 | 3724.8577 | 3970.3172 | 4063.9205 | 4330.4831 | 4430.4086
| 900 | 3711.1654 | 4036.8013 | 4294.3749 | 4386.2101 | 4677.3169 | 4789.1028 | 5104.6935 | 5225.0407 | 5567.764 | 5696.2397 | Type 22 ►
| Km | 0.48385 | 0.5455 | 0.59078 | 0.61433 | 0.62564 | 0.61176 | 0.62274 | 0.60873 | 0.61948 | 0.60708
| n | 1.3798 | 1.371 | 1.3666 | 1.3623 | 1.3735 | 1.3848 | 1.396 | 1.4072 | 1.4185 | 1.429
| Test report | ENE/MRT.RES.15019 | ENE/MRT.RES.15019 | ENE/MRT.RES.15019 | ENE/MRT.RES.15019 | ENE/MRT.RES.15019 | ENE/MRT.RES.15019 | ENE/MRT.RES.15019 | ENE/MRT.RES.15019 | ENE/MRT.RES.15019 | ENE/MRT.RES.15019
2%

## TUTTI_VERT (hidden)
ID | 10VP1400 | 10VP1500 | 10VP1600 | 10VP1700 | 10VP1800 | 10VP1900 | 10VP2000 | 10VP2100 | 10VP2200 | 10VP2300 | 10VP2400 | 20VP1400 | 20VP1500 | 20VP1600 | 20VP1700 | 20VP1800 | 20VP1900 | 20VP2000 | 20VP2100 | 20VP2200 | 20VP2300 | 20VP2400 | 21VP1400 | 21VP1500 | 21VP1600 | 21VP1700 | 21VP1800 | 21VP1900 | 21VP2000 | 21VP2100 | 21VP2200 | 21VP2300 | 21VP2400 | 22VP1400 | 22VP1500 | 22VP1600 | 22VP1700 | 22VP1800 | 22VP1900 | 22VP2000 | 22VP2100 | 22VP2200 | 22VP2300 | 22VP2400 | 10VL1400 | 10VL1500 | 10VL1600 | 10VL1700 | 10VL1800 | 10VL1900 | 10VL2000 | 10VL2100 | 10VL2200 | 10VL2300 | 10VL2400 | 20VL1400 | 20VL1500 | 20VL1600 | 20VL1700 | 20VL1800 | 20VL1900 | 20VL2000 | 20VL2100 | 20VL2200 | 20VL2300 | 20VL2400 | 21VL1400 | 21VL1500 | 21VL1600 | 21VL1700 | 21VL1800 | 21VL1900 | 21VL2000 | 21VL2100 | 21VL2200 | 21VL2300 | 21VL2400 | 22VL1400 | 22VL1500 | 22VL1600 | 22VL1700 | 22VL1800 | 22VL1900 | 22VL2000 | 22VL2100 | 22VL2200 | 22VL2300 | 22VL2400
Modello | 10VP | 10VP | 10VP | 10VP | 10VP | 10VP | 10VP | 10VP | 10VP | 10VP | 10VP | 20VP | 20VP | 20VP | 20VP | 20VP | 20VP | 20VP | 20VP | 20VP | 20VP | 20VP | 21VP | 21VP | 21VP | 21VP | 21VP | 21VP | 21VP | 21VP | 21VP | 21VP | 21VP | 22VP | 22VP | 22VP | 22VP | 22VP | 22VP | 22VP | 22VP | 22VP | 22VP | 22VP | 10VL | 10VL | 10VL | 10VL | 10VL | 10VL | 10VL | 10VL | 10VL | 10VL | 10VL | 20VL | 20VL | 20VL | 20VL | 20VL | 20VL | 20VL | 20VL | 20VL | 20VL | 20VL | 21VL | 21VL | 21VL | 21VL | 21VL | 21VL | 21VL | 21VL | 21VL | 21VL | 21VL | 22VL | 22VL | 22VL | 22VL | 22VL | 22VL | 22VL | 22VL | 22VL | 22VL | 22VL
Mod. | Profilata verticale 10 | Profilata verticale 10 | Profilata verticale 10 | Profilata verticale 10 | Profilata verticale 10 | Profilata verticale 10 | Profilata verticale 10 | Profilata verticale 10 | Profilata verticale 10 | Profilata verticale 10 | Profilata verticale 10 | Profilata verticale 20 | Profilata verticale 20 | Profilata verticale 20 | Profilata verticale 20 | Profilata verticale 20 | Profilata verticale 20 | Profilata verticale 20 | Profilata verticale 20 | Profilata verticale 20 | Profilata verticale 20 | Profilata verticale 20 | Profilata verticale 21 | Profilata verticale 21 | Profilata verticale 21 | Profilata verticale 21 | Profilata verticale 21 | Profilata verticale 21 | Profilata verticale 21 | Profilata verticale 21 | Profilata verticale 21 | Profilata verticale 21 | Profilata verticale 21 | Profilata verticale 22 | Profilata verticale 22 | Profilata verticale 22 | Profilata verticale 22 | Profilata verticale 22 | Profilata verticale 22 | Profilata verticale 22 | Profilata verticale 22 | Profilata verticale 22 | Profilata verticale 22 | Profilata verticale 22 | Linear Verticale 10 | Linear Verticale 10 | Linear Verticale 10 | Linear Verticale 10 | Linear Verticale 10 | Linear Verticale 10 | Linear Verticale 10 | Linear Verticale 10 | Linear Verticale 10 | Linear Verticale 10 | Linear Verticale 10 | Linear Verticale 20 | Linear Verticale 20 | Linear Verticale 20 | Linear Verticale 20 | Linear Verticale 20 | Linear Verticale 20 | Linear Verticale 20 | Linear Verticale 20 | Linear Verticale 20 | Linear Verticale 20 | Linear Verticale 20 | Linear Verticale 21 | Linear Verticale 21 | Linear Verticale 21 | Linear Verticale 21 | Linear Verticale 21 | Linear Verticale 21 | Linear Verticale 21 | Linear Verticale 21 | Linear Verticale 21 | Linear Verticale 21 | Linear Verticale 21 | Linear Verticale 22 | Linear Verticale 22 | Linear Verticale 22 | Linear Verticale 22 | Linear Verticale 22 | Linear Verticale 22 | Linear Verticale 22 | Linear Verticale 22 | Linear Verticale 22 | Linear Verticale 22 | Linear Verticale 22
TR | ENE/MRT.RES.00012a | ENE/MRT.RES.00012a | ENE/MRT.RES.00012a | ENE/MRT.RES.00012a | ENE/MRT.RES.00012a | ENE/MRT.RES.00012a | ENE/MRT.RES.00012a | ENE/MRT.RES.00012a | ENE/MRT.RES.15025 | ENE/MRT.RES.00012a | ENE/MRT.RES.15025 | ENE/MRT.RES.00012c | ENE/MRT.RES.00012c | ENE/MRT.RES.00012c | ENE/MRT.RES.00012c | ENE/MRT.RES.00012c | ENE/MRT.RES.00012c | ENE/MRT.RES.00012c | ENE/MRT.RES.00012c | ENE/MRT.RES.15026 | ENE/MRT.RES.00012c | ENE/MRT.RES.15026 | ENE/MRT.RES.00012d | ENE/MRT.RES.00012d | ENE/MRT.RES.00012d | ENE/MRT.RES.00012d | ENE/MRT.RES.00012d | ENE/MRT.RES.00012d | ENE/MRT.RES.00012d | ENE/MRT.RES.00012d | ENE/MRT.RES.15027 | ENE/MRT.RES.00012d | ENE/MRT.RES.15027 | ENE/MRT.RES.15019 | ENE/MRT.RES.15019 | ENE/MRT.RES.15019 | ENE/MRT.RES.15019 | ENE/MRT.RES.15019 | ENE/MRT.RES.15019 | ENE/MRT.RES.15019 | ENE/MRT.RES.15019 | ENE/MRT.RES.15019 | ENE/MRT.RES.15019 | ENE/MRT.RES.15019 | ENE/MRT.RES.00015a | ENE/MRT.RES.00015a | ENE/MRT.RES.00015a | ENE/MRT.RES.00015a | ENE/MRT.RES.00015a | ENE/MRT.RES.00015a | ENE/MRT.RES.00015a | ENE/MRT.RES.00015a | ENE/MRT.RES.15021 | ENE/MRT.RES.00015a | ENE/MRT.RES.15021 | ENE/MRT.RES.00015b | ENE/MRT.RES.00015b | ENE/MRT.RES.00015b | ENE/MRT.RES.00015b | ENE/MRT.RES.00015b | ENE/MRT.RES.00015b | ENE/MRT.RES.00015b | ENE/MRT.RES.00015b | ENE/MRT.RES.15022 | ENE/MRT.RES.00015b | ENE/MRT.RES.15022 | ENE/MRT.RES.00015c | ENE/MRT.RES.00015c | ENE/MRT.RES.00015c | ENE/MRT.RES.00015c | ENE/MRT.RES.00015c | ENE/MRT.RES.00015c | ENE/MRT.RES.00015c | ENE/MRT.RES.00015c | ENE/MRT.RES.15023 | ENE/MRT.RES.00015c | ENE/MRT.RES.15023 | ENE/MRT.RES.15020 | ENE/MRT.RES.15020 | ENE/MRT.RES.15020 | ENE/MRT.RES.15020 | ENE/MRT.RES.15020 | ENE/MRT.RES.15020 | ENE/MRT.RES.15020 | ENE/MRT.RES.15020 | ENE/MRT.RES.15020 | ENE/MRT.RES.15020 | ENE/MRT.RES.15020
Altezza | 1400 | 1500 | 1600 | 1700 | 1800 | 1900 | 2000 | 2100 | 2200 | 2300 | 2400 | 1400 | 1500 | 1600 | 1700 | 1800 | 1900 | 2000 | 2100 | 2200 | 2300 | 2400 | 1400 | 1500 | 1600 | 1700 | 1800 | 1900 | 2000 | 2100 | 2200 | 2300 | 2400 | 1400 | 1500 | 1600 | 1700 | 1800 | 1900 | 2000 | 2100 | 2200 | 2300 | 2400 | 1400 | 1500 | 1600 | 1700 | 1800 | 1900 | 2000 | 2100 | 2200 | 2300 | 2400 | 1400 | 1500 | 1600 | 1700 | 1800 | 1900 | 2000 | 2100 | 2200 | 2300 | 2400 | 1400 | 1500 | 1600 | 1700 | 1800 | 1900 | 2000 | 2100 | 2200 | 2300 | 2400 | 1400 | 1500 | 1600 | 1700 | 1800 | 1900 | 2000 | 2100 | 2200 | 2300 | 2400
RESA canale a 50 | 47 | 0 | 52.54 | 0 | 58.62 | 0 | 65.17 | 0 | 72.4 | 76.19 | 80.2 | 72.07 | 0 | 81.13 | 0 | 90 | 0 | 98.67 | 0 | 107.2 | 111.36 | 115.5 | 89.15 | 0 | 98.03 | 0 | 106.74 | 0 | 115.33 | 0 | 123.8 | 128.08 | 132.3 | 109.1 | 113.9 | 118.8 | 124 | 129.3 | 134.9 | 140.6 | 146.6 | 152.8 | 159.2 | 165.9 | 42.33 | 0 | 46.15 | 0 | 50.78 | 0 | 56.18 | 0 | 62.5 | 66.08 | 69.9 | 63.99 | 0 | 72.06 | 0 | 80.73 | 0 | 89.95 | 0 | 99.9 | 105.19 | 110.6 | 82.02 | 0 | 89.92 | 0 | 97.51 | 0 | 104.85 | 0 | 112 | 115 | 118.9 | 105.9 | 111.5 | 117 | 122.3 | 127.6 | 132.7 | 137.7 | 142.6 | 147.4 | 152.1 | 156.7
n | 1.363 |  | 1.3494 |  | 1.3357 |  | 1.351 |  | 1.3663 | 1.374 | 1.382 | 1.3127 |  | 1.3105 |  | 1.3083 |  | 1.3132 |  | 1.3181 | 1.3206 | 1.323 | 1.2943 |  | 1.3221 |  | 1.3499 |  | 1.3446 |  | 1.3394 | 1.3368 | 1.3354 | 1.3798 | 1.3754 | 1.371 | 1.3666 | 1.3623 | 1.3735 | 1.3848 | 1.396 | 1.4072 | 1.4185 | 1.429 | 1.2341 |  | 1.2886 |  | 1.3431 |  | 1.3303 |  | 1.3176 | 1.3112 | 1.309 | 1.263 |  | 1.2768 |  | 1.2905 |  | 1.2858 |  | 1.2812 | 1.2789 | 1.276 | 1.2985 |  | 1.3176 |  | 1.3368 |  | 1.3414 |  | 1.346 | 1.3483 | 1.352 | 1.3544 | 1.3548 | 1.3551 | 1.3554 | 1.3557 | 1.3566 | 1.3575 | 1.3583 | 1.3592 | 1.3677 | 1.3761
km | 0.22702 |  | 0.26791 |  | 0.31535 |  | 0.33017 |  | 0.34529 | 0.35277 | 0.35991 | 0.42421 |  | 0.48167 |  | 0.53895 |  | 0.57958 |  | 0.6175 | 0.63548 | 0.6529 | 0.56376 |  | 0.5561 |  | 0.54319 |  | 0.59904 |  | 0.65655 | 0.68601 | 0.71255 | 0.49372 | 0.5243 | 0.55663 | 0.59078 | 0.62687 | 0.62564 | 0.62424 | 0.62274 | 0.62115 | 0.61948 | 0.61947 | 0.33887 |  | 0.29848 |  | 0.26544 |  | 0.30857 |  | 0.3611 | 0.39118 | 0.41737 | 0.45736 |  | 0.48813 |  | 0.51828 |  | 0.58805 |  | 0.66481 | 0.70669 | 0.7514 | 0.51038 |  | 0.51911 |  | 0.52228 |  | 0.55157 |  | 0.57863 | 0.58997 | 0.60003 | 0.52925 | 0.5566 | 0.58322 | 0.60918 | 0.63443 | 0.65766 | 0.68019 | 0.702 | 0.72318 | 0.72196 | 0.71956
[9 empty] | B |  | B | [8 empty] | B |  | B | [8 empty] | B |  | B | [19 empty] | B |  | B | [8 empty] | B |  | B | [8 empty] | B |  | B